Explanatory note of Electrical Network

Preface

Sketch design for the object “Technical project of new bridge over the Venta river and of access roads, Ventspils” has been developed on the bases of order issued by Ventspils City Council as of 8.04.2005, designing task Nr 34 and as of 28.11.2005, designing task Nr 76 and 77.

Design of electrical supply part has been developed on the bases of technical regulations Nr 30R4E0 – 01/615 issued by JSC “Latvenergo” Ventspils Western electrical network as of April 24, 2007.

Expected time of construction – year 2008.

Used output data

Geodesy

Works of geodesic survey were carried out by SIA “ĢEODĒZISTS” in digital system. Survey is made in LKS-92TM coordination system and in Baltic height system.

The designed engineering networks

The designing works were carried out according construction regulations, regulations and general norms being in force in the Latvian Republic.

10 kV cable networks

To install two transition connection pairs, put in the trench cable AXCEL-24-3x240 and build joint caps on the end of cables. Install cables in previously designed protective pipe places (see in Fabrikas street technical project).

To install one transition connection pair, put in the trench cable AXCEL-24-3x240 and built joint caps on the end of cables.  To install new plastic protective pipes ø160mm over the new access road opposite Rupniecibas Street Nr.27.

0,4 kV power electrical networks

To maintain and to protect all the existing cables of 0,4 kV and 10 kV. In the intersections to install the reserve protective pipes of diameter of D110mm. In case of necessity for the existing power cables there have to be installed the renovation pipes.

Street lighting

To install street and bridge lighting by embedding cable AXMK – 4x50 in the trench from the previously designed lighting cable board (design of Rūpniecības street) till the last designed pole of Fabrikas street.  To install the metal poles of H=8,0m with 150w lighting armature Nr.1 – Nr.26. The poles Nr.9-14 must be installed at the bridge constructions, installation of cable in the section of bridge must be in the plastic protective pipe.  Pole Nr 1 is fed with cable AXMK-4x16 from the cable board.

Reserve protective pipe for the section of bridge

For the installation of reserve cables along the bridge constructions in the whole length of bridge (at the opposite side of the lighting cable) there must be installed plastic pipe of D110mm.

Supplement

Under the carriageway of the street and in the intersections with other communications, the cables must be installed in the plastic protective pipes of “AROT”. In all crossings there must be installed reserve pipes.

In case of questions please contact author of the project.

Author:                      K.Draviņš