EXPLANATORY NOTE

- 1. General data

The project part has been developed according norms and regulations being in force in LR, as well as observing technical regulations issued by operating organisations.

The external network are according regulations – LBN 223-99, LBN 222-99

For the work out of the project there are used topographical and archive materials as well as made inspection of object at site. In the project part there are developed drawings of external network.

Before inception of construction works there must be invited all representatives from the interested organisations for reason to specify the location of existing engineer network at site. During the construction of the designed engineering networks there must be considered conditions at site and in case of necessity to correct the place of installation of the engineering networks beforehand coordinating it with the author of project.

During the construction works there must be provided protection and strengthening of existing and newly built in engineering networks.

The mounting works and inspection is carried out according CN 3.05.04-85, as well as observing technical indications of suppliers of material and equipment.

In the project part there are developed drawings of external network.

2. Sewerage of rain water

In the project there is expected to construct new rain water duct from the bridge over the Venta river till the previously designed rain water sewage network of Fabrika street and new rain water duct from the new bridge till previously designed rain water sewage network of Rūpniecības street. Diameter of the designed rain water sewage collector is 250mm. Depth and fall of rain water duct is designed observing relief of streets and crossings with communications. It is expected to construct collection pits (gullies) with settling part. Diameter of connecting pipe of collection pits is 200mm.

The pipes must be embedded on blinding of compacted sand of 15 cm. The trench must be filled with grunt (if clayey particles are <5%), and then compacted till natural level of density. Compacting must be carried out in 20-30cm thick layer. Compacting must be done with hand vibrant-rammer. In the zone along pipes compacting must be carried out without mechanisms. Pipes must be embedded in dry trench. Works are forbidden to carry out in wet trench. For the pump out of ground water from the trench there must be used movable immersed drainage pump or for the lowering of level of ground water there have to be used ground water lowering facility with needle filters.

3. Water pipe

In the project it is expected to connect the previously designed water pipe at Fabrikas street with the previously designed water pipe of Rūpniecības street. The water main is expected to be constructed from water supply pressure-pipes PE PN10 with diameter of D200mm. Depth of embedding is h=1,50 – 1,60m. Over the bridge it is expected to construct water pipe from Upolar heat isolated pressure-pipe PE PN10 of diameter D200/315mm. Fastenings of water pipes on the bridge see in “Construction part”. In the highest point of the bridge on the water pipe it is expected to install automatic bleeding. At the both ends of the bridge we expect wells with fire fighting hydrants and water pipe emptying valve, and drainage to the nearest rain water sewage pit.

The pipes must be embedded on blinding of compacted sand of 15 cm. The trench must be filled with grunt (if clayey particles are <5%), and then compacted till natural level of density. Compacting must be carried out in 20-30cm thick layer. Compacting must be done with hand vibrant-rammer. In the zone along pipes compacting must be carried out without mechanisms. Pipes must be embedded in dry trench.

Remarks:

1. In the section of street in the crossing with the existing cable route, for the cables there must be expected establishment of double case-pipe. During the construction there must be ensured exploitation of the pipes.  To provide protection of unearthed cables by unbinding them to the beam placed across the trench.

2. Class of pipe embedding is T8.

Engineer                                            A. Urtāns