General instructions for electrical network

The designing works are carried out according construction regulations, regulations and general norms being in force in the Latvian Republic.

The construction works have to be carried out according work project, Latvian construction regulations and observing technical regulations of object.

Coordination system is LKS-92 TM, height remarks – Baltic height system according data of SIA «ĢEODĒZISTS».

Before inception of construction works there must be invited all representatives from the interested organisations for reason to specify the location of existing engineer network at site. During the construction of the designed engineering networks there must be considered conditions at site and in case of necessity to correct the place of installation of the engineering networks beforehand coordinating it with the author of project.

During the construction works there must be provided protection and strengthening of existing and newly built in engineering networks. In the distance of 2 m from the engineering networks and trees the excavation works have to be carried out without mechanisms. In places, where bushes of trees or roots hinder execution of construction works, the works have to be carried out according appendix “Activities for protection of uncovered roots of trees at the site”. Sawing of branches of the trees has to be coordinated with Greening Maintenance Work group of City Council.

Before establishment of street coverage, all underground engineering networks have to be installed. Attraction of the engineering networks is given from axle line of the street. Due to this reason before installation of engineering networks there should be outlined axle line of the street.

During the construction there have to be observed the following order of construction works: 1 – installation of water main, household sewerage and rain water duct; 2 – removal of spare ground under the carriageway, parking places and sidewalks; 3 – installation of communication network;  4 – installation of electrical networks.

The current depth of telephone networks is assumed 0,7-1,0 metres form ground surface, but current depth of electrical cables is assumed  0,7 metres from ground surface.

The trenches have to be filled with sand with admixture of clayey particles lesser than 5%.

All dimensions are in mm. Height remarks, distances and radius are in m. Declivity is in %.

In case of some questions please contact author of the project.

- Indications for installation of electrical networks

To obey general regulations.

Embedding depths of cables is 0,7 m from the ground surface, but in places of crossing the carriageway - 1.0 m.

The current and designed cables under the carriageway which intersect with other engineering networks have to be installed in plastic pipes. In the junctions there have to be installed additional reserve plastic pipes.

At the cable board, lighting pole and sleeves the cable must be installed in ground together with hasps.

The designed engineering networks have to be installed on sand base of 100mm, covered with 200mm thick sand layer (compacting (E=30MPa) at 200mm thick layers) and have to be covered with red warning plastic protective tape.

All parts of metal, non-conducting power, and of electrical devices which due to damage of isolation can be under the power have to be earthed.

Author: K.Draviņš