## Battery_capacity_ALC_Intellia
[9 empty] | Battery capacity too low | Battery capacity OK
Battery capacity calculation table FX / Intellia
Product Codes |  |  |  | Pcs | Standby current mA | Alarm current mA | Standby current mA | Alarm current mA
See Comm. | Panels and options |  | FX, FXL and FXM (incl. MC and UI) | 1 | 65 | 105 | 65 | 105
00703810 |  |  | FXS (incl. MC and UI) | 0 | 60 | 100 | 0 | 0
See Comm. |  |  | FX, FXL and FXM (incl. MC2 and UI2) | 0 | 135 | 171 | 0 | 0
00703814 |  |  | FXS (incl. MC2 and UI2) | 0 | 125 | 161 | 0 | 0
00702515 |  |  | ALCA | 0 | 54 | 54 | 0 | 0
00702517 |  |  | ALCB | 2 | 78 | 78 | 156 | 156
00702512 |  |  | CLC | 0 | 20 | 20 | 0 | 0
|  | current consumption/line | -EOL 4,7kΩ | 0 | 5.6 | 60 | 0 | 0
|  | current consumption/line | -EOL 2,94kΩ | 0 | 8.1 | 60 | 0 | 0
|  | current consumption/line | -normally closed contact | 0 | 15.6 | 60 | 0 | 0
00702530 |  |  | IOC | 0 | 20 | 20 | 0 | 0
00702531 |  |  | OCA | 0 | 3 | 3 | 0 | 0
00702520 |  |  | SAA | 0 | 20 | 20 | 0 | 0
00702521 |  |  | SAB | 0 | 40 | 40 | 0 | 0
00702522 |  |  | SAC | 0 | 60 | 60 | 0 | 0
00703833 |  |  | REPX-OB | 0 | 40 | 40 | 0 | 0
00703835 |  |  | MCOX-OB | 0 | 40 | 40 | 0 | 0
00702541 | Current of 1 LED is ~1mA, in this calculation it is assumed that there is fire indicated in one FX panel |  | FX-LB32 | 0 | 1 | 2 | 0 | 0
00702542 | Current of 1 LED is ~1mA, in this calculation it is assumed that there is fire indicated in one zone |  | FX-LB80 | 0 | 1 | 2 | 0 | 0
00409910 |  |  | CFD-900 | 0 | 75 | 120 | 0 | 0
| Total, Panels and options | [5 empty] | 221 | 261
00396010 | Devices that are powered |  | FMP | 1 | 22 | 42 | 22 | 42
00703831 | from the FX panel |  | FMPX | 0 | 40 | 75 | 0 | 0
00392200 |  |  | MCO | 0 | 25 | 25 | 0 | 0
00703834 |  |  | MCOX | 0 | 50 | 50 | 0 | 0
00392100 |  |  | REP | 0 | 25 | 25 | 0 | 0
00703832 |  |  | REPX | 0 | 50 | 50 | 0 | 0
06431220 |  |  | MPO | 0 | 115 | 115 | 0 | 0
06432501 |  |  | IAS1 | 0 | 300 | 300 | 0 | 0
00703840 | 50 LEDs on at the same time, |  | ZLPX | 0 | 50 | 72 | 0 | 0
other configurations should be calculated separately
| Other devices eg. Fire transmitter – conv fire alarm devices… |  |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
| Total, External devices | [5 empty] | 22 | 42
Detectors
06720210 | Ion smoke detector |  | EDI-10 |  | 0.5 | (3,5)* | 0 | 0
06720220 | Optical smoke detector |  | EDI-20 | 0 | 0.4 | (3,4)* | 0 | 0
06720230 | Photo -thermal detector |  | EDI-30 | 69 | 0.5 | (3,5)* | 34.5 | 34.5
06720250 | Thermal detector |  | EDI-50 | 0 | 0.5 | (3,5)* | 0 | 0
06720260 | CO detector |  | EDI-60 | 0 | 0.5 | (3,5)* | 0 | 0
06720262 | Configurable Carbon Monoxide Heat Multisensor |  | 58000-305APO | 0 | 0.47 | (3,5)* | 0 | 0
06720011 | Short circuit isolator base |  | EBI-11 | 0 | 0.4 | (4,0)* | 0 | 0
06725283 | Base Mounted Flame Detector UV |  | 55000-022APO | 0 | 2.3 | 4.2 | 0 | 0
06725284 | Base Mounted Flame Detector UV/Dual IR |  | 55000-023APO | 0 | 2.8 | 4.2 | 0 | 0
06725285 | Base Mounted Flame Detector Triple IR |  | 55000-024APO | 0 | 2.5 | 4.2 | 0 | 0
06725270 | Beam detector |  | 55000-268APO | 0 | 5 | (9,0)* | 0 | 0
06725271 | Beam detector |  | 55000-273APO | 5 | 5 | (9,0)* | 25 | 25
06725280 | Flame detector |  | 55000-280APO | 0 | 2.2 | (4,2)* | 0 | 0
Call points
06723732 | Manual call point, with isolator |  | EPP-20 | 15 | 0.3 | (5,0)* | 0 | 0
06723735 | Manual call point, with isolator |  | EPP-21 | 0 | 0.3 | (5,0)* | 0 | 0
Alarm devices
06728010 | Base sounder |  | ESI-10 (85dB) | 0 | 0.1 | 3 | 0 | 0
|  |  | ESI-10 (70dB) | 0 | 0.1 | 1.3 | 0 | 0
06728020 | Addressable base sounder, with isolator |  | ESI-20 (91dB) | 0 | 0.3 | 5 | 0 | 0
|  |  | ESI-20 (78dB) | 0 | 0.3 | 2.1 | 0 | 0
06728030 | Addressable base sounder |  | ESI-30 (91dB) | 0 | 0.3 | 5 | 0 | 0
|  |  | ESI-30 (78dB) | 0 | 0.3 | 2.1 | 0 | 0
06728040 | Addressable sounder (100dB) |  | ESI-40 (100dB) | 26 | 1.2 | 5 | 31.2 | 130
|  |  | ESI-40 (92dB) | 0 | 1.2 | 3.1 | 0 | 0
06728050 | Addressable sounder (100dB) |  | ESI-50 (100dB) | 0 | 1.2 | 5 | 0 | 0
|  |  | ESI-50 (92dB) | 0 | 1.2 | 3.1 | 0 | 0
06728106 | Addressable sounder (92/100dB) |  | ESI-52 (92/100dB) | 0 | 0.3 | 5 | 0 | 0
06728107 | Addressable sounder beacon (92/100dB) |  | ESI-53 (92/100dB) | 0 | 0.3 | 8 | 0 | 0
06728107 | Addressable beacon |  | ESI-54 | 0 | 0.3 | 3.1 | 0 | 0
06728060 | Sounder strobe, with isolator |  | ESI-60 (91dB) | 0 | 0.3 | 8 | 0 | 0
|  |  | ESI-60 (78dB) | 0 | 0.3 | 2.1 | 0 | 0
06728070 | Sounder strobe |  | ESI-70 (91dB) | 0 | 0.3 | 8 | 0 | 0
|  |  | ESI-70 (78dB) | 0 | 0.3 | 2.1 | 0 | 0
06728080 | Beacon base |  | ESI-80 | 0 | 0.15 | 3 | 0 | 0
06728118 | Configurable Open area sounder beacon |  | Volume level 7 (100dB(A)) | 0 | 0.45 | 8.5 | 0 | 0
06728117 | Configurable Sounder beacon base |  | Volume level 7 (90dB(A)) | 0 | 0.43 | 8.5 | 0 | 0
Control and monitoring devices, Surface mount models
06727310 | Monitor module, 1 input |  | EMI-310 | 0 | 1 | (4,0)* | 0 | 0
06727340 | Monitor module, 1 input |  | EMI-310+ | 0 | 1 | (4,0)* | 0 | 0
06727341 | Conventional zone module |  | EMI-310/CZ | 0 | 6 | 21 | 0 | 0
06727311 | Control module, 1 input, 1 output |  | EMI-311 | 20 | 1.25 | (5,5)* | 25 | 25
06727361 | 240V Relay control unit |  | EMI-311/240 | 0 | 1.5 | 5 | 0 | 0
06727301 | Control module, 1 output |  | EMI-301 | 0 | 0.4 | 1.8 | 0 | 0
06727351 | Sounder control module |  | EMI-301/S | 0 | 1.7 | 50 | 0 | 0
06727372 | Mini control module, 1 input |  | Mini Switch Monitor | 0 | 0.2 | (6,4)* | 0 | 0
06727333 | I/O module, 1 input, 1 output (3 relay contacts in parallel) |  | EMI-333 | 0 | 3 | (7,5)* | 0 | 0
Control and monitoring devices, DIN-rail models
06727400 | Isolator module, 2 isolators |  | EMI-400 | 0 | 0.47 | 4 | 0 | 0
06727410 | Monitor module, 1 input |  | EMI-410 | 0 | 0.7 | (3,4)* | 0 | 0
06727440 | Control module, 1 input |  | EMI-410+ | 0 | 1 | (5,6)* | 0 | 0
06727441 | Conventional zone module |  | EMI-410/CZ | 0 | 6 | 21 | 0 | 0
06727411 | I/O module, 1 input, 1 output |  | EMI-411 | 0 | 1.2 | (6,0)* | 0 | 0
06727401 | Control module, 1 output |  | EMI-401 | 0 | 0.7 | 3.3 | 0 | 0
06727451 | Sounder control module |  | EMI-401/S | 0 | 1.9 | 50 | 0 | 0
Xpander Wireless
06726023 | Xpander Loop Interface (31 addresses) |  | Xpander | 0 | 15 | 15 | 0 | 0
06720601 | Remote LED (output from detector limited to 5mA) |  | ERI-10 | 33 | 0 | 5 | 0 | 25
| Device LED alarm current (max 5 devices with LEDs on at the same time)* | [6 empty] | 17.5
| Total number of field devices |  |  | 168
| Loop components in total | [5 empty] | 115.7 | 257
| Current consumption in total | [5 empty] | 358.7 | 560
Battery capacity = (L1 x T1 + L2 x T2) x 1,25 Ah
| L1 = Standby current | 0.3587 | A | Battery capacity |  |  | 22.7688 | Ah |  | Battery capacity OK
| T1 = Battery backup time | 50 | h | Charge time (hours) |  |  | 5.498 | h
| L2 = Alarm device current | 0.56 | A | Chosen Battery capacity |  |  | 102 | Ah
| T2 = Alarm time | 0.5 | h | Backup time with chosen batteries |  |  | 226.7076 | h
(Actual standby time)
Note on A6: FXNET 00703612 FXLNET 00703712 FXMNET 00703822
Note on A8: FX 3NET 00703600 FXLNET 00703700 FXMNET 00703800

## Notes! (hidden)
Date | Note
2012-02-08 | ALC_Loop_length row 68 short circuit load (mA) is the load that a sc isolator causes when it send a current pulse to see if sc is still in the loop.
Apollo has specified the load to be 60 - 100mA per isolator.
2010-06-16 | LC + SLC Conventional loop modules current consumption value:
On loop length calc. = only comm. + LED current
On Battery calc. = comm. + LED + max. Sub.loop load

## BC_LC_SLC (hidden)
WMSOU-RR-P35 | 06711730 | High volume | 0.12 | 6.72
WSO-PR-N33 | 06711738 | Medium volume | 0.12 | 2.69
|  | Low volume | 0.12 | 1.39
WMSOU-RR-P36 | 06711731 | High volume | 0.22 | 6.82
WSO-PSO-I33 | 06711737 | Medium volume | 0.22 | 2.79
|  | Low volume | 0.22 | 1.49
WMSST-RR-P35 | 06711732 | High volume | 0.12 | 6.72
WSS-PR-N33 | 06711740 | Medium volume | 0.12 | 4.92
|  | Low volume | 0.12 | 3.6
WMSST-RR-P36 | 06711733 | High volume | 0.22 | 6.82
WSS-PR-I33 | 06711739 | Medium volume | 0.22 | 5.02
|  | Low volume | 0.22 | 3.7
WMSTR-WR-P35 | 06711734 | Strobe | 0.12 | 2.22
WST-PR-N33 | 06711736
WMSTR-WR-P36 | 06711735 | Strobe, with isolator | 0.22 | 2.22
WST-PR-I33 | 06711741
IBSOU-DD-P35 (grey) | 06711712 | High volume | 0.11 | 6.41
IBSOU-PW-P35 (white) | 06711716 | Medium volume | 0.11 | 2.22
BSO-PP-N33 | 06711722 | Low volume | 0.11 | 1.16
IBSOU-DD-P36 (grey) | 06711713 | High volume | 0.22 | 6.52
IBSOU-PW-P36 (white) | 06711717 | Medium volume | 0.22 | 2.33
BSO-PP-I33 | 06711721 | Low volume | 0.22 | 1.27
IBSST-DR-P35 (grey) | 06711714 | High volume | 0.11 | 8.61
IBSST-PR-P35 (white) | 06711718 | Medium volume | 0.11 | 4.44
BSS-PR-N33 | 06711724 | Low volume | 0.11 | 3.69
IBSST-DR-P36 (grey) | 06711715 | High volume | 0.22 | 8.72
IBSST-PR-P36 (white) | 06711719 | Medium volume | 0.22 | 4.55
BSS-PR-I33 | 06711723 | Low volume | 0.22 | 3.7

## LL_ALC (hidden)
Configurable Open area sounder beacon
Volume level 1 (60dB(A)) | 0.45 | 4
Volume level 2 (69dB(A)) | 0.45 | 4.4
Volume level 3 (75dB(A)) | 0.45 | 4.6
Volume level 4 (81dB(A)) | 0.45 | 5
Volume level 5 (87dB(A)) | 0.45 | 5.6
Volume level 6 (93dB(A)) | 0.45 | 6.6
Volume level 7 (100dB(A)) | 0.45 | 8.5
Configurable Sounder beacon base
Volume level 1 (60dB(A)) | 0.43 | 4
Volume level 2 (70dB(A)) | 0.43 | 4.3
Volume level 3 (74dB(A)) | 0.43 | 4.6
Volume level 4 (78dB(A)) | 0.43 | 5.1
Volume level 5 (82dB(A)) | 0.43 | 5.8
Volume level 6 (86dB(A)) | 0.43 | 7
Volume level 7 (90dB(A)) | 0.43 | 8.5

## Log (hidden)
Change log
Date | Version |  | Changes
2012-10-15 | ver. 66571746GB6 -> GB7 |  | Isolator R values of the devices added to version GB6 now added to calculations.
R additions to:
SLC_Loop_length
ALC_Loop_lentgh
Isolator DEN values of the devices added to version GB6 now added to calculations.
DEN additions to:
Isolators_LC
2012-09-20 | ver. 66571746GB5 -> GB6 |  | Following Alarm Devices:
BSO-PP-I33 DETECTOR BASE SOUNDER
BSO-PP-N33 DETECTOR BASE SOUNDER NON_ISO
BSS-PR-I33 DET BASE SOUNDER STROBE ISO
BSS-PR-N33 DET BASE SOUNDER STROBE NON-ISO
WSO-PR-I33 WALL MOUNT SOUNDER ISO
WSO-PR-N33 WALL MOUNT SOUNDER NON-ISO
WSS-PR-I33 WALL MOUNT SOUNDER STROBE ISO
WSS-PR-N33 WALL MOUNT SOUNDER STROBE NON-ISO
WST-PR-I33 WALL MOUNT STROBE ISO
WST-PR-N33 WALL MOUNT STROBE NON-ISO
have been added to:
Battery_capacity_LC_SLC
Battery_capacity_LC_SLC_ALC
SLC_Loop_length
Volume settings (High, Medium, Low) for these added sounders are done with Drop Down List
Carbon Monoxide Heat Multisensor, Configurable Open Area Sounder Beacon, Configurable Sounder Beacon Base added to:
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
ALC_Loop_lentgh
Isolators_ALC
Volume settings (Levels 1 - 7) for these added sounders are done with Drop Down List
2012-03-01 | ver. 66571746GB4 -> GB5 |  | EPP-20 added to short circuit calculation.
ALC_Loop_lentgh
FX, FXL and FXM (incl. MC2 and UI2) and FXS (incl. MC2 and UI2) -panels added to:
Battery_capacity_LC_SLC
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
2012-02-08 | ver. 66571746GB3 -> GB4 |  | Short circuit load (mA) (on row 68) changed from 120mA to 60mA. Load of 120mA is not likely to happen in a case of short circuit.
ALC_Loop_lentgh
SySe AP200 Beams EB6500A and EB6500SA added to:
Battery_capacity_LC_SLC
Battery_capacity_LC_SLC_ALC
SLC_Loop_length
Isolator resistances of addressable sounders were not summed to 'Total resistance of isolators'. Now fixed in:
SLC_Loop_length
LC_Loop_length
ALC_Loop_lentgh (only EMI-400 was missing)
Isolator base B524IEFT-1 and isolator module EM200XE added to:
LC_Loop_length
Isolator module EM200XE added to:
Battery_capacity_LC_SLC
Battery_capacity_LC_SLC_ALC
Isolator base EBI-11 added to:
ALC_Loop_lentgh
A few extra rows for extra devices such as conventional alarm devices and Fire transmitter added to:
Battery_capacity_LC_SLC
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
2011-09-26 | ver. 66571746GB2 -> GB3 |  | Apollo addressable alarm devices ESI-52, ESI-53 and ESI-54 added
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
ALC_Loop_lentgh
2011-05-20 | ver. 66571746GB1 -> GB2 |  | Product codes column added
Battery_capacity_LC_SLC
Battery_capacity_ALC_Intellia
Apollo flame detectors added
- Base Mounted Flame Detector UV
- Base Mounted Flame Detector UV/Dual IR
- Base Mounted Flame Detector Triple IR
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
ALC_Loop_lentgh
SySe addressable alarm devices
different current consumptions for different volume levels added
- WMSTR-WR-P35
- WMSTR-WR-P36
- WMSST-RR-P35
- WMSST-RR-P36
- WMSOU-RR-P35
- WMSOU-RR-P36
- IBSST-DR-P35
- IBSST-DR-P36
- IBSOU-DD-P35
- IBSOU-DD-P36
Battery_capacity_LC_SLC
Battery_capacity_LC_SLC_ALC
SLC_Loop_length
LC_Loop_length
Apollo addressable alarm devices
different current consumptions for different volume levels added
- ESI-10
- ESI-20
- ESI-30
- ESI-40
- ESI-50
- ESI-60
- ESI-70
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
ALC_Loop_lentgh
6 -> 8V max voltage drop
SLC_Loop_Length
2010-10-18 | ver.66571746GB0 -> GB1 |  | ESI-80 added
Battery_capacity_ALC_Intellia
Battery_capacity_LC_SLC_ALC
ALC_Loop_length
Isolators_ALC
2010-06-16 | ver.110510 -> 6657 1746GB0 |  | Version numbering changed to correspond to normal Pelco document numbering.
Battery_capacity_LC_SLC
- Remote LED and device LED separated to own rows
|  |  | - WMSOU-RR-P01 | -> | WMSOU-RR-P35
|  |  | - WMSOU-RR-P02 | -> | WMSOU-RR-P36
|  |  | - WMSST-RR-P01 | -> | WMSST-RR-P35
|  |  | - WMSST-RR-P02 | -> | WMSST-RR-P36
|  |  | - WMSTR-RR-P01 | -> | WMSTR-RR-P35
|  |  | - WMSTR-RR-P02 | -> | WMSTR-RR-P36
|  |  | - IBSOU-DD-P01 | -> | IBSOU-DD-P35
|  |  | - IBSOU-DD-P02 | -> | IBSOU-DD-P36
|  |  | - IBSST-DR-P01 | -> | IBSST-DR-P35
|  |  | - IBSST-DR-P02 | -> | IBSST-DR-P36
- EM210E-CZ standby current value changed 0,5 -> 3,5mA
- M512ME standby current value changed 0,3 -> 7,0mA
- M512ME alarm current value changed 55,1 -> 60,0mA
- EM210E-CZ standby current value changed 0,5 -> 3,5mA
- EM210E-CZR standby current value changed 0,5 -> 4,2mA
Battery_capacity_ALC
- Remote LED and device LED separated to own rows
- Xpander Wireless Interface added
Battery_capacity_LC_SLC_ALC
- Remote LED and device LED separated to own rows
- Xpander Wireless Interface added
|  |  | - WMSOU-RR-P01 | -> | WMSOU-RR-P35
|  |  | - WMSOU-RR-P02 | -> | WMSOU-RR-P36
|  |  | - WMSST-RR-P01 | -> | WMSST-RR-P35
|  |  | - WMSST-RR-P02 | -> | WMSST-RR-P36
|  |  | - WMSTR-RR-P01 | -> | WMSTR-RR-P35
|  |  | - WMSTR-RR-P02 | -> | WMSTR-RR-P36
|  |  | - IBSOU-DD-P01 | -> | IBSOU-DD-P35
|  |  | - IBSOU-DD-P02 | -> | IBSOU-DD-P36
|  |  | - IBSST-DR-P01 | -> | IBSST-DR-P35
|  |  | - IBSST-DR-P02 | -> | IBSST-DR-P36
- EM210E-CZ standby current value changed 0,5 -> 3,5mA
- M512ME standby current value changed 0,3 -> 7,0mA
- M512ME alarm current value changed 55,1 -> 60,0mA
- EM210E-CZ standby current value changed 0,5 -> 3,5mA
- EM210E-CZR standby current value changed 0,5 -> 4,2mA
LC_Loop_length
- Remote LED and device LED separated to own rows
|  |  | - WMSOU-RR-P01 | -> | WMSOU-RR-P35
|  |  | - WMSOU-RR-P02 | -> | WMSOU-RR-P36
|  |  | - WMSST-RR-P01 | -> | WMSST-RR-P35
|  |  | - WMSST-RR-P02 | -> | WMSST-RR-P36
|  |  | - WMSTR-RR-P01 | -> | WMSTR-RR-P35
|  |  | - WMSTR-RR-P02 | -> | WMSTR-RR-P36
|  |  | - IBSOU-DD-P01 | -> | IBSOU-DD-P35
|  |  | - IBSOU-DD-P02 | -> | IBSOU-DD-P36
|  |  | - IBSST-DR-P01 | -> | IBSST-DR-P35
|  |  | - IBSST-DR-P02 | -> | IBSST-DR-P36
- EM210E-CZ alarm current value changed 17,7 -> 2,7mA
- M512ME alarm current value changed 55,1 -> 5,1mA
- EM210E-CZ alarm current value changed 17,7 -> 2,7mA
- EM210E-CZR alarm current value changed 62,7 -> 2,7mA
- EM210E-CZ alarm current calculation equation changed =(MIN(D66;3)+INT((D66-MIN(D66;10))/10))*F66 -> =D66*E66 (cells H66 and H78)
- EM210E-CZR alarm current calculation equation changed =(MIN(D79;3)+INT((D79-MIN(D79;10))/10))*F79 -> =D79*E79
SLC_Loop_length
- Remote LED and device LED separated to own rows
|  |  | - WMSOU-RR-P01 | -> | WMSOU-RR-P35
|  |  | - WMSOU-RR-P02 | -> | WMSOU-RR-P36
|  |  | - WMSST-RR-P01 | -> | WMSST-RR-P35
|  |  | - WMSST-RR-P02 | -> | WMSST-RR-P36
|  |  | - WMSTR-RR-P01 | -> | WMSTR-RR-P35
|  |  | - WMSTR-RR-P02 | -> | WMSTR-RR-P36
|  |  | - IBSOU-DD-P01 | -> | IBSOU-DD-P35
|  |  | - IBSOU-DD-P02 | -> | IBSOU-DD-P36
|  |  | - IBSST-DR-P01 | -> | IBSST-DR-P35
|  |  | - IBSST-DR-P02 | -> | IBSST-DR-P36
- EM210E-CZ alarm current value changed 17,7 -> 2,7mA
- EM210E-CZR alarm current value changed 62,7 -> 2,7mA
- EM210E-CZ alarm current calculation equation changed =(MIN(D39;3)+INT((D39-MIN(D39;10))/10))*F39 -> =D39*E39
- EM210E-CZR alarm current calculation equation changed =(MIN(D40;3)+INT((D40-MIN(D40;10))/10))*F40 -> =D40*E40
ALC_Loop_length
- Remote LED and device LED separated to own rows
- Xpander Wireless Interface added
- EMI-310/CZ alarm current calculation equation changed =(MIN(D30;3)+INT((D30-MIN(D30;10))/10))*F30 -> =D31*E31
- EMI-410/CZ alarm current calculation equation changed =(MIN(D41;3)+INT((D41-MIN(D41;10))/10))*F41 -> =D42*E42
Isolators_LC
- Indication (with *) of devices that also have isolators, but can be installed without or that there is also a non isolated version
Isolators_ALC
- Xpander Wireless Interface added
2010-05-11 | ver.070510 -> ver.110510 |  | Isolators_LC
- 200-series modules added to sheet.
- Note: "* Indicates that the device includes a short circuit isolator but in this calculation is considered to be installed without it." added
Isolators_ALC
- ESI-81 added
- Xpander Loop Interface added
ALC_Loop_length
- ESI-81 added
- Xpander Loop Interface added
Battery_capacity_LC_SLC_ALC
- ESI-81 added
- Xpander Loop Interface added
Battery_capacity_ALC
- ESI-81 added
- Xpander Loop Interface added
2010-05-07 | ver.040510 -> ver.070510 |  | LC_Loop_length
- Loop calculation equation typing error:
#N/A
2010-05-04 | ver.230410 -> ver.040510 |  | Battery_capacity_LC_SLC
- ASD1 -> IAS1
Battery_capacity_ALC_Intellia
- ASD1 -> IAS1
Battery_capacity_LC_SLC_ALC
- ASD1 -> IAS1
LC_Loop_length
- Average duty cycle factor added (0,8)
- Max voltage drop value changed 7,5V -> 6V
SLC_Loop_length
- Average duty cycle factor added (0,9)
- Max voltage drop value changed 7,5V -> 6V
Isolators_LC
- Devices with isolators removed
- 17V and 7V unnecessary texts removed